Date:      May 26, 2025

Title:      RFP #20251313266 Fire Alarm, Sprinkler & Suppression System Inspections

Subject: Questions and Answers

- Can you please provide a device inventory for the fire alarm devices, sprinkler system, foam systems, kitchen hood systems, fire pumps, standpipe systems, main drains, fire department connections, AHU shutdowns, and any other devices or equipment we need include in the RFP?

Device and system inventories were provided to all vendors who attended the mandatory pre-proposal conference via email on Wednesday, May 21, 2025.

- Section 11 Inspection Grid.  EP.20 was not listed in the RFP.  Does this mean that rolling and sliding doors are covered by another RFP?

The inspection requirements for EP20 of the Joint Commission Standards for fire doors are not included in this inspection RFP. This inspection RFP includes the testing of the fire door components that are tied to the Fire Alarm System. The testing expectations of these devices is covered in EP4 of the Joint Commission Standards.

Fire Door Components to Test (Tied to Fire Alarm System):

- Electromagnetic Releasing Devices and Door Holds

  - Ensure they release automatically upon fire alarm activation, allowing the door to close.

- Door Unlock Mechanisms (e.g., Maglocks, Electrified Strikes)

  - Maglocks and Electrified Strikes must de-energize upon fire alarm activation, allowing the door to open freely for egress.

  - Verify that these devices fail-safe, meaning they release upon loss of power or fire alarm signal.

Fire Alarm System Functions to Verify:

- Control Panel Integration

  - Verify that the fire door release relays or circuits are activated properly by the fire alarm control panel.

- Zone Activation

  - Confirm door release is triggered from appropriate initiating devices (e.g., smoke detectors in the same zone).

- Section 11 Inspection Grid.  EP.12 is a 5-year test.  What year will it be required to be tested?

The Date of the last inspection for EP 12 was provided in the email sent to all vendors on Wednesday, May 21, 2025.

- Section 11 Inspection Grid.  EP.16 is for annual inspection of fire extinguishers was not listed in the RFP.  Does this mean that they are covered by another RFP?

The inspection of the fire extinguisher’s is not included in the RFP.

- We were told that we would receive inspection reports for the systems so that we could accurately price the requested inspections. Please provide.

Device and system inventories were provided to all vendors who attended the mandatory pre-proposal conference via email on Wednesday, May 21, 2025.

- We would like to request an extension to this bid so that we can have an ample amount of time to present JPS/Tarrant County with the most competitive price possible.

I’m agreeable to providing an additional week moving the closeout date to June 9, 2025 for vendors to prepare their submissions.

All corrections, changes, additions, revisions, and/or clarifications in this Addendum #1 to the

RFP are hereby made a part of RFP #20251313266 Fire Alarm, Sprinkler & Suppression System Inspections.

All Respondents to the RFP shall acknowledge receipt and acceptance of this Addendum #1 by

signing in the space provided and submitting the signed Addendum #1 with the RFP.

Proposals submitted without an executed copy of this Addendum #1 attached may be considered

informal and may be rejected.

Received, acknowledged, and conditions agreed to on this _________ day of _________, 2025, by:

Respondent:  __________________________________________________________

Company Name: _______________________________________________________

If there are questions pertaining to this addendum please contact  Bid_submissions@jpshealth.org