Date:     February 27, 2026

Title:    RFP #25-0917 Construction Manager At-Risk for JPS Campus Fiber Loop Project

Subject: Addendum #1

- Regarding JPS Fiber Loop Letter_Addendum_Sealed. pdf document, were there any other structural assessments performed on any other structures besides the Medical Examiner’s Building that are referenced in the RFP?

  - ANSWER(S): Yes. Original and Revised Structural reports have information on other buildings.  Burns to send to JPS documents to ensure accuracy.

- Please clarify and/or provide the specific testing requirements that JPS is requiring for Section 271323 - Communications Optical Fiber Backbone Cabling?

  - ANSWER(S): Refer to specification section 27 13 23 _Communications Optical Fiber Backbone Cabling.  Section 2  - Products.

- Regarding the JPS Campus Fiber Loop Project Drawing Set Addendum 1 -1-13-2026, page 1 – phasing notes – Phase 1-2 sections…please provide clarification on the preferred method of termination for the transition from TDU to the IDF riser fiber?

  - ANSWER(S): Fiber Loop contractor will terminate fiber from CUP to each MDF or main entry IDF within a Fiber Enclosure (Corning Edge solution).  Using LC/LC duplex connectors on adapters for Edge Fiber Field-Term cassettes.  JPS IT and/or GC for new construction will patch over to building (new/existing) fiber riser to each IDF room. Refer to sheet TC601.

- Regarding the JPS Campus Fiber Loop Project Drawing Set Addendum 1 -1-13-2026, page 1 – phasing notes phase 1-2 sections…will the MFP project contractor be required to install conduits to the hand-hole being placed by the JPS fiber loop project contractor or only to the exterior of the building only?

  - ANSWER(S): New Building Construction – Fiber Loop contractor to connect to conduits from each new building which is outside of the building footprint provided and installed by new building GC.  Existing Buildings – Fiber Loop contractor will provide conduits as shown within documents for entry into the various existing buildings along with supporting cabling infrastructure to Fiber Enclosure location within MDF and/or entry termination IDF for each building. Refer to structural report for designated penetrations locations.

- Regarding the JPS Campus Fiber Loop Project Drawing Set Addendum 1 -1-13-2026, page 1 – Installation Procedure Section…Are these procedures being provided for informational purposes only or what are the expectations for the contractor from JPS regarding this section?

  - ANSWER(S): Installation procedures shown are per manufacturer recommendations and best practices for a successful project. (Sumitomo).  If not selected, then Fiber Loop contractor must comply and adhere to manufacturer installation and best practice methods.

- Regarding section 270543 – Underground Ducts and Raceways for Communications. There is direct reference to electrical division 26 sections 0543 and 0533.13 versus explicit compliance with TIA-758-B (OSP) and TIA-569-D (communications pathways) … is this compliance acceptable by JPS?

  - ANSWER(S): Yes. Compliance with TIA is mandatory along with comply with DIV 26 and NEC codes.

- Regarding section 270543 – Underground Ducts and Raceways for Communications. Are there any requirements for “mandrel testing” in the ABF tubes after installation?

ANSWER(S): Yes. Mandrel testing is required to ensure tubing pathways are free of defects and have a smooth transition from CUP (Data Center ) to each MDF and/or entry termination IDF for each building.

- Does JPS have specific requirements for “as-built and splice documentation” for all phase of the project?

  - ANSWER(S): Yes. As-builts and any splice documentation must be noted for record.  Just to note: Splicing is a last resort if distance exceeds fiber reel lengths and only by JPS IT approval prior to preform splicing (Fusion Splicing).

- Regarding Tab 2, question 1 of the Proposal Requirements,  a. Provide a statement of qualifications listing, at a minimum, the content provided in the AIA A305 Contractor Qualifications Statement. Must we include our complete AIA A305 in the proposal, and does it count towards our 50-page max? Our AIA A305 alone is 24 pages.

  - ANSWER(S): Please complete the AIA A305 document. No, it does not count towards the 50-page max.

All corrections, changes, additions, revisions, and/or clarifications in this Addendum #1 to the

RFP are hereby made a part of the RFP #25-0917 Construction Manager At-Risk for JPS Campus Fiber Loop Project.

All Respondents to the RFP shall acknowledge receipt and acceptance of this Addendum #1 by

signing in the space provided and submitting the signed Addendum #1 with the RFP.

Proposals submitted without an executed copy of this Addendum #1 attached may be considered

informal and may be rejected.

Received, acknowledged, and conditions agreed to on this _________ day of _________, 2026, by:

Respondent:  __________________________________________________________

Company Name: _______________________________________________________

If there are questions pertaining to this addendum, please contact Bid_submissions@jpshealth.org.